## 1. LOS Asset Hierarchy Template
Service | Program Service Objectives | Community Levels of Service | Service Division | Supporting Asset Classes | Target Asset Levels of Service (by Asset Class) | Current Asset Levels of Service
[6 empty] | Asset Class Average | Distribution by Asset Rating
[7 empty] | % | % | % | % | %
[5 empty] | Condition | Condition
[5 empty] | Performance | Performance
[5 empty] | Condition | Condition
[5 empty] | Performance | Performance
[5 empty] | Condition | Condition
[5 empty] | Performance | Performance
[5 empty] | Condition | Condition
[5 empty] | Performance | Performance
[5 empty] | Condition | Condition
[5 empty] | Performance | Performance
[5 empty] | Condition | Condition
[5 empty] | Performance | Performance
Note on A1: Consistent with Asset hierarchy
Note on B1: A general service statement reflecting the desired level of service to the customer. Sources: Strategic Plan, Council Directive. See examples in the catalogue
Note on C1: General service statements on what the customer expects to receive from the service. See examples in the catalogue.
Note on D1: Should be consistent with asset hierarchy
Note on E1: Should be consistent with asset hierarchy
Note on F1: Refer to Condition Rating and General Performance Rating sheets for ratings and recommended targets.
Note on G2: The averaged level of service for the asset class.
Note on H2: Breakdown of the assets per the ratings and ranges on the Condition Rating and General Performance Rating sheets.

## 2. LOS Asset Hierarchy eg Water
Service | Program Service Objectives | Community Levels of Service | Service Division | Supporting Asset Classes | Target Asset Levels of Service (by Asset Class) | Current Asset Levels of Service
[6 empty] | Asset Class Average | Distribution by Asset Rating
[7 empty] | % | % | % | % | %
Water | Safe, reliable and efficient potable water services | Consistent and reliable water supply | Distribution | Local Watermains | Condition | Condition
[5 empty] | 3 breaks/km lifetime | 2 break/km |  | 70 | 10 | 20
[5 empty] | Performance | Performance
[5 empty] | Operational Functionality = Good | Good |  | 100
[5 empty] | Capacity = Good | Good |  | 100
[5 empty] | Operational Resiliency = Good | Good |  | 100
|  |  |  | Pumping Stations | Condition | Condition
[5 empty] | Mechanical Process Systems = "Good" | Fair |  |  | 100
[5 empty] | Electrical Process Systems = "Good" | Fair |  |  | 100
[5 empty] | Distribution Civil Assets = "Good" | Fair |  |  | 100
|  | Safe and aesthetically pleasing water quality |  |  | Performance | Performance
[5 empty] | Operational Functionality = Good | Good |  | 60 | 40
[5 empty] | Capacity = Good | Good |  | 60 | 40
[5 empty] | Operational Resiliency = Good | Good |  | 100
[5 empty] | Environmental Resiliency = Good | Poor |  |  | 50 | 50
|  |  |  | Treated Water Storage | Condition | Condition
[5 empty] | Distribution Civil Assets = "Good" | Fair |  |  | 80 | 20
[5 empty] | Performance | Performance
[5 empty] | Operational Functionality = Good |  |  | 100
[5 empty] | Capacity = Good |  |  | 100
[5 empty] | Operational Resiliency = Good |  |  | 100
[5 empty] | Environmental Resiliency = Good |  |  | 100
|  | The system is efficiently designed and managed | Treatment | Intake | Condition | Condition
[5 empty] | Mechanical Systems = "Good" | Fair |  |  | 100
[5 empty] | Electrical Process Systems = "Good" | Fair |  |  | 100
[5 empty] | Civil Treatment Assets = "Good" | Good |  | 100
[5 empty] | Performance | Performance
[5 empty] | Operational Functionality = Good | Good |  | 100
[5 empty] | Capacity = Good | Good |  | 100
[5 empty] | Operational Resiliency = Good | Good |  | 100
[5 empty] | Environmental Resiliency = Good | Good |  | 100
|  |  |  | Pre-Treatment | Condition | Condition
[5 empty] | Mechanical Process Systems = "Good" | Fair |  |  | 100
[5 empty] | Electrical Process Systems = "Good" | Fair |  |  | 100
[5 empty] | Civil Treatment Assets = "Good" | Good |  | 100
|  | The water system is kept in good condition |  |  | Performance | Performance
[5 empty] | Operational Functionality = Good | Good |  | 100
[5 empty] | Capacity = Good | Good |  | 100
[5 empty] | Operational Resiliency = Good | Good |  | 100
[5 empty] | Environmental Resiliency = Good | Good |  | 100
|  |  |  | Primary Treatment | Condition | Condition
[5 empty] | Mechanical Process Systems = "Good" | Good | 50 | 50
[5 empty] | Electrical Process Systems = "Good" | Good | 50 | 50
[5 empty] | Civil Treatment Assets = "Good" | Good |  | 100
[5 empty] | Performance | Performance
[5 empty] | Operational Functionality = Good | Good |  | 100
[5 empty] | Capacity = Good | Good |  | 100
[5 empty] | Operational Resiliency = Good | Good |  | 100
[5 empty] | Environmental Resiliency = Good | Good |  | 100
Note on A1: Consistent with Asset hierarchy
Note on B1: A general service statement reflecting the desired level of service to the customer. Sources: Strategic Plan, Council Directive. See examples in the catalogue
Note on C1: General service statements on what the customer expects to receive from the service. See examples in the catalogue.
Note on D1: Should be consistent with asset hierarchy
Note on E1: Should be consistent with asset hierarchy
Note on F1: Refer to Condition Rating and General Performance Rating sheets for ratings and recommended targets.
Note on G2: The averaged level of service for the asset class.
Note on H2: Breakdown of the assets per the ratings and ranges on the Condition Rating and General Performance Rating sheets.

## 3. Serv Object CLOS Statements
Service | Examples of Service Objective Statements | Examples of Community Levels of Service
Water | Safe, reliable and efficient potable water services | Consistent and reliable water supply
Safe and aesthetically pleasing water quality
The system is efficiently designed and managed
The water system is kept in good condition

## 4, Cond Ratings Water
Asset Types | Notes for Determining Asset Levels of Service | Asset Condition Ratings and Corresponding Likelihood of Failure1, 2, 3 |  |  |  |  | Additional Notes
|  | Likelihood of Failure Very Unlikely (Estimated beyond 20 yrs. or >10%) | Likelihood of Failure Unlikely (Estimated in 11-20 yrs. or 10%-30%) | Likelihood of Failure Possible (Estimated in 6-10 yrs. or 30%-60%) | Likelihood of Failure Likely (Estimated in 1-5 yrs. or 60%-90%) | Likelihood of Failure Very Likely or Certain (Estimated in less than 1 yr. or Now or <90%)
- Transmission mains - Feedermains - Local Watermains | A target of "Good" or ERUSL = 11-20 years (when estimating condition based on age) is recommended for Feedermain and Transmission mains due to a variety of factors: - a high importance to community services - a significant risk liability (health and safety, environment, financial cost, municipal reputation) - the potential complexities and additional time necessary to plan and design the replacement of Feedermains (say >5 years) - have a high value requiring time to accumulate necessary financing for full replacement, reconstruction or rehabilitation (say >5 years) - the potentially significant financial value requiring extra time to accumulate necessary financing for full replacement (say >5 years) A target of "Fair" or ERUSL = 6-10 years (when estimating condition based on age) may be considered for Local Watermains due to a variety of factors: - a moderate importance to service delivery - a moderate risk liability (health and safety, environment, financial cost, municipal reputation) - there is little complexity or uniqueness to the asset thus requiring less planning and design time (< 5 years) - a moderate or low value to replace the asset thus requiring a shorter time to accumulate financing (say < 5 years) - proactive rehabilitation strategies are generally not cost effective or non-existent and the asset is better suited to a straightforward replacement. | Use for pipes with an ERUSL greater than 20 years Estimated by any of the following (see notes on Tab A: "Options on Rating Watermains"). - pipe age and material - number/projected number of breaks/km of pipe - hours/projected hours of unplanned service interruptions per service connection - electromagnetic pipe assessments | Use for pipes with an ERUSL = 11 to 20 years. Estimated by any of the following (see notes on Tab A: "Options on Rating Watermains"). - pipe age and material - number/projected number of breaks/km of pipe - hours/projected hours of unplanned service interruptions per service connection - electromagnetic pipe assessments | Use for pipes with an ERUSL = 6 to 10 years. Estimated by any of the following (see notes on Tab A: "Options on Rating Watermains"). - pipe age and material - number/projected number of breaks/km of pipe - hours/projected hours of unplanned service interruptions per service connection - electromagnetic pipe assessments | Use for pipes with an ERUSL = 1 to 5 years. Estimated by any of the following (see notes on Tab A: "Options on Rating Watermains"). - pipe age and material - number/projected number of breaks/km of pipe - hours/projected hours of unplanned service interruptions per service connection - electromagnetic pipe assessments | Use for pipes with an ERUSL less than year or beyond ERUSL or are currently failing acceptable service requirements. Estimated by any of the following (see notes on Tab A: "Options on Rating Watermains"). - pipe age and material - number/projected number of breaks/km of pipe - hours/projected hours of unplanned service interruptions per service connection - electromagnetic pipe assessments | When using asset age to estimate asset condition, consider maintaining a conservative estimate of the total useful service life until such time as condition assessments data becomes available. Notwithstanding the O.Reg. reporting requirements, municipalities have discretion on how to rate and set ALOS targets on the condition of linear water assets. See notes on Tab A: "Options on Rating Watermains".
Water treatment and distribution mechanical and electrical assets such as pumps, motors, motor control centres, centrifuges, conveyors, skimmers, scrapers, bridges, generator units etc. as part of: - Pumping Stations/Pumping Systems - Pre-Treatment Systems - Primary Treatment Systems/ Disinfection Systems/Filtration Systems - Water Storage Systems - Standby Power | Targets, ranges and descriptions intended for assets with an estimated useful service life of at least 20 years. A target of "Good" or ERUSL = 11-20 years (when estimating condition based on age) is recommended for the assets/asset systems due to a variety of factors: - a significant to high importance to community services - a significant risk liability (health and safety, environment, financial cost, municipal reputation) - the potential complexities and additional time necessary to plan and design the replacement or rehabilitation of the assets/asset systems (say >5 years) - the potentially significant financial value of the assets/asset systems requiring extra time to accumulate necessary financing for possible full replacement or reconstruction (say >5 years) - some assets can benefit from rehabilitation strategies to extend asset life and defer reconstruction/replacement costs before the assets become too worn or dysfunctional to make such strategies feasible - the assets/assets systems may be expensive to operate and need to be efficient to minimize costs A target of "Fair" or ERUSL = 6-10 years (when estimating condition based on age) may be considered due to a variety of factors: - a moderate or low importance to service delivery - a moderate or low risk liability (health and safety, environment, financial cost, municipal reputation) - there is little complexity or uniqueness to the assets/asset systems thus requiring less planning and design time (< 5 years) - a moderate or low value to replace, reconstruct or rehabilitate the assets/asset systems thus requiring a shorter time to accumulate necessary financing (say < 5 years) - proactive rehabilitation strategies are generally not cost-effective or non-existent and the assets/asset systems are better suited to a straightforward change-out or replacement. - Operating costs are relatively low | The assets are rated 'Very Good'. - Fit for the future. - Well maintained, in good condition, new or recently rehabilitated. - Minor defects and/or wear AND/OR ERUSL>20 years (When estimating condition based on age or according to condition assessment information) | The assets are rated 'Good'. - Adequate for now. - Modest defects and/or wear. AND/OR ERUSL = 11-20 years (When estimating condition based on age or according to condition assessment information) | The assets are rated 'Fair'. - Shows signs of deterioration and some elements exhibit deficiencies. - May require attention. - Moderate defects and/or wear AND/OR ERUSL= 6-10 years (When estimating condition based on age or according to condition assessment information) | The assets are rated 'Poor'. - An increasing potential for asset conditions to affect the services it (or they) provides. - Approaching the end of service life. - The condition is below the standard and a large portion of the system (or asset) exhibits significant deterioration. - Significant defects and/or wear. AND/OR ERUSL is 1-5 years (When estimating condition based on age or according to condition assessment information) | The assets are rated 'Very Poor'. - Unfit for sustained service. - Near or beyond its expected service life and shows widespread signs of advanced deterioration. - The asset or some assets may be unusable. - Severe defects and/or wear AND/OR ERUSL <1 year or beyond EURSL (When estimating condition based on age or according to condition assessment information) | Where municipalities may not already have their own rating system for mechanical and electrical assets this is an optional rating system that can be used or modified. To be used on assets with an estimated service life of at least 20 years. Determine asset conditions using available data, including: - Age and estimated remaining useful service life - Visual inspections - Condition assessments/testing of electrical and mechanical equipment - Maintenance history When using asset age to estimate asset condition, consider maintaining a conservative estimate of the total useful service life until such time as condition assessments data becomes available. The evaluation descriptions (except in italics) are consistent with the "2019 Canadian Infrastructure Report Card". The defect/wear descriptions (in italics) and ERUSLs are for additional information. There is no requirement under O.Reg 588/17 for reporting these assets using this ALOS rating system; however, an ALOS rating and reporting system will be required to meet the future reporting requirements under O.Reg 588/17.
Water treatment, distribution and storage civil assets such as: - In-ground reservoirs - Elevated storage, - Process treatment tanks/channels, - Surge protection systems/tanks - Pumping Station gallery areas/substructures (Excluding building envelope (see Building ALOS)), | Targets, ranges and descriptions intended for assets with an estimated useful service life of at least 20 years. A target of "Good" or ERUSL = 11-20 years (when estimating condition based on age) is recommended for the assets/asset systems due to a variety of factors: - a significant to high importance to community services - a significant risk liability (health and safety, environment, financial cost, municipal reputation) - the potential complexities and additional time necessary to plan and design the replacement or rehabilitation of the assets/asset systems (say >5 years) - the potentially significant financial value of the assets/asset systems requiring extra time to accumulate necessary financing for possible full replacement or reconstruction (say >5 years) - some assets can benefit from rehabilitation strategies to extend asset life and defer reconstruction/replacement costs before the assets become too worn or dysfunctional to make such strategies feasible - the assets/assets systems may be expensive to operate and need to be efficient to minimize costs A target of "Fair" or ERUSL = 6-10 years (when estimating condition based on age) may be considered due to a variety of factors: - a moderate or low importance to service delivery - a moderate or low risk liability (health and safety, environment, financial cost, municipal reputation) - there is little complexity or uniqueness to the assets/asset systems thus requiring less planning and design time (< 5 years) - a moderate or low value to replace, reconstruct or rehabilitate the assets/asset systems thus requiring a shorter time to accumulate necessary financing (say < 5 years) - proactive rehabilitation strategies are generally not cost-effective or non-existent and the assets/asset systems are better suited to a straightforward change-out or replacement. - Operating costs are relatively low | The assets are rated 'Very Good'. - Fit for the future. - Well maintained, in good condition, new or recently rehabilitated. - Minor defects and/or wear AND/OR ERUSL>20 years (When estimating condition based on age or according to condition assessment information) | The assets are rated 'Good'. - Adequate for now. - Modest defects and/or wear. AND/OR ERUSL = 11-20 years (When estimating condition based on age or according to condition assessment information) | The assets are rated 'Fair'. - Shows signs of deterioration and some elements exhibit deficiencies. - May require attention. - Moderate defects and/or wear AND/OR ERUSL= 6-10 years (When estimating condition based on age or according to condition assessment information) | The assets are rated 'Poor'. - An increasing potential for asset conditions to affect the services it (or they) provides. - Approaching the end of service life. - The condition is below the standard and a large portion of the system (or asset) exhibits significant deterioration. - Significant defects and/or wear. AND/OR ERUSL is 1-5 years (When estimating condition based on age or according to condition assessment information) | The assets are rated 'Very Poor'. - Unfit for sustained service. - Near or beyond its expected service life and shows widespread signs of advanced deterioration. - The asset or some assets may be unusable. - Severe defects and/or wear AND/OR ERUSL <1 year or beyond EURSL (When estimating condition based on age or according to condition assessment information) | Where municipalities may not already have their own rating system for civil/structural assets this is an optional rating system that can be used or modified. To be used on assets with an estimated service life of at least 20 years. Determine asset conditions using available data, including: - Age and estimated remaining useful service life - Visual inspections - Condition assessments/testing of electrical and mechanical equipment - Maintenance history When using asset age to estimate asset condition, consider maintaining a conservative estimate of the total useful service life until such time as condition assessments data becomes available. The evaluation descriptions (except in italics) are consistent with the "2019 Canadian Infrastructure Report Card". The defect/wear descriptions (in italics) and ERUSLs are for additional information. There is no requirement under O.Reg 588/17 for reporting these assets using this ALOS rating system; however, an ALOS rating and reporting system will be required to meet the future reporting requirements under O.Reg 588/17.
*Notes: 1. | Likelihood of Failure is based on the estimated remaining timespan that assets, asset components or asset systems are expected to function at levels that are still adequate, safe, reliable and viable to provide desired Community Levels of Service (CLOS) but at increasing levels of risk as assets/asset components degrade as the end of service life approaches. The total lifespan of an asset often extends beyond estimated useful service life; however, the assets may no longer be sufficient, safe, viable, economical or reliable to provide safe and desired community services. Note that Likelihood of Failure provides high level estimates for strategic risk assessments purposes and can vary on an asset by asset basis according the environment, soil conditions, design, materials and use.
2. | Condition ranges and Likelihood of Failure estimates are intended for strategic analysis and planning and can vary by municipality and by the assets themselves according design, construction, materials, use and environmental conditions.
3. | ERUSL = Estimated remaining useful service life.

## 5, General Performance Ratings
Asset Performance Ratings and Corresponding Likelihood of Failure (All Assets)1, 2
LoF | Very Unlikely Current Likelihood of Failure >10% | Unlikely Current Likelihood of Failure = 10%-30% | Possible Current Likelihood of Failure = 30%-60% | Likely Current Likelihood of Failure = 60%-90% | Very Likely or Certain Current Likelihood of Failure <90%
Perf. | VERY GOOD | GOOD | FAIR | POOR | VERY POOR
General Descrip. | Exceeds or fully meets performance requirements. No affect to services | Meets performance requirements. No affect to services | Just meets performance requirements with some limitations Minor or no perceivable affects to services. | Does not meet several performance requirements in whole or in part. Perceivable and/or sporadic affects to services | Does not meet many or most performance requirements as a whole. Moderate or significant and/or ongoing affects to services.
Operational Functionality | - Fully meets or exceeds current minimum community service level requirements in a fully efficient and effective manner. - Exceeds minimum current design and/or safety requirements - No operational problems experienced. - No affects on community service levels or stakeholders - Fully complies with current Regulations and/or Standards3. - No desirable elements are missing, and all required elements are present. - Technology is state-of-the art/best available - Resource consumption: 100% of baseline efficiency | - Meets current minimum community service level requirements in an efficient and effective manner. - Meets minimum current design and/or safety requirements - Occasional operational problems may be experienced. - No noticeable affects on overall community service levels and/or stakeholders - Complies with Regulations and/or Standards3 with possibly some "grandfathering" where permitted by Regulation for certain standards. - A few desirable elements may be missing, but all required elements are present. - Technology is industry standard - Resource consumption: 91% to 100% of baseline efficiency | - Just meets/essentially satisfies the current minimum community service level requirements with possibly occasional or minor constraints, and/or some inefficiencies and ineffectiveness present. - Just meets minimum current design and/or safety requirements possibly with some added monitoring, extra controls or maintenance. - Operational problems may occur more frequently. - There may be some minor affects to community service levels and/or stakeholders - Meets essential Regulations and/or Standards3 with "grandfathering" where permitted by Regulation for certain standards. - A few desirable elements and one or two required elements are missing. - Technology is adequate but may not be efficient. - Resource consumption: 76 to 90% of baseline efficiency | - A limited ability to meet current minimum community service level requirements with performance frequently below minimum service and efficiency requirements. - Does not fully meet minimum current design and/or safety requirements in whole or in part. Significant monitoring, extra controls or maintenance actions may be required to maintain community services. - Significant operational problems are evident and occur frequently with perceivable and possibly moderate affects to community services - May not meet or partially meets essential Regulations and/or Standards3 which may not be permitted "grandfathering" by Regulation or are unsafe or impractical to continue "grandfathering" - Several desirable elements and one or two required elements are missing. - Technology is nearing obsolescence. May be inefficient, prone to breakdown with no vendor support or original equipment manufacturer parts available. - Resource consumption: 51 to 75% of baseline efficiency | - Ability to meet current minimum community service level requirements is deficient and unsustainable with performance significantly and continuously below minimum service and efficiency requirements. - Does not most or all meet minimum current design and/or safety requirements in whole. Monitoring, extra controls or maintenance actions are not practical or feasible to maintain community services. - Operational problems are serious and ongoing and affecting community services. - Does not meet essential or critical Regulations and/or Standards3, and "grandfathering" cannot be permitted either by Regulation or due to safety or practical concerns. - Many desirable and several required elements are missing. - Technology is obsolete and/or non-functional and replacement parts may be unavailable - Resource consumption: Less than 50% of baseline efficiency
Capacity to Meet Demands | - Capacity fully meets or exceeds current demands and minimum community service level requirements - No operational problems experienced. - No affects on community service levels or stakeholders | - Capacity meets current demands and minimum community service level requirements - Minor and occasional operational problems may be experienced. - No noticeable affects on overall community service levels and/or stakeholders | - Capacity just meets/essentially satisfies current demands and minimum community service level requirements, possibly with occasional or minor constraints and/or reduced efficiency. - Operational problems may occur more frequently. - There may be some minor or modest affects to community service levels and/or stakeholders | - Capacity is frequently below demands and/or minimum community service level requirements. - Significant operational problems are evident and can occur frequently. - There are noticeable and possibly moderate affects to community service levels and/or stakeholders. | - Capacity is significantly and continuously below demands and/or minimum community service level requirements. - Operational problems are serious and ongoing. - There are noticeable and possibly significant affects to community service levels and/or stakeholders.
Operational Resiliency | - Fully meets or exceeds the minimum emergency or service safeguard requirements for back-up systems, spare capacity, alternative supply or system/asset security. - Maximum protection or security from acts of vandalism, trespassing, theft, assault or terrorism. | - Meets the minimum emergency or service safeguard requirements for back-up systems, spare capacity, alternative supply or system/asset security. - Adequate protection or security from acts of vandalism, trespassing, theft, assault or terrorism. | - Provides acceptable but limited emergency or service safeguard requirements for back-up systems, spare capacity, alternative supply or system/asset security. - Reasonable but limited protection or security from acts of vandalism, trespassing, theft, assault or terrorism. | - Provides partial but inadequate emergency or service safeguard requirements for back-up systems, spare capacity, alternative supply or system/asset security. - Partial protection or security from acts of vandalism, trespassing, theft, assault or terrorism. | - Provides marginal or no emergency or service safeguard requirements for back-up systems, spare capacity, alternative supply or system/asset security. - Marginal or no protection or security from acts of vandalism, trespassing, theft, assault or terrorism.
Environmental Resiliency | - Assets are fully resilient to environmental stresses; e.g. impacts from wind, fire, flooding, excessive rainfall/snowfall etc.. - Fully meets climate change mitigation requirements. | - Assets are adequately resilient to environmental stresses; e.g. impacts from wind, fire, flooding, excessive rainfall/snowfall etc.. - Meets almost all climate change mitigation requirements. | - Assets are resilient with some limitations to environmental stresses; e.g. impacts from wind, fire, flooding, excessive rainfall/snowfall etc.. - Provides acceptable but limited protections from climate change. | - Asset resiliency to environmental stresses is partially lacking; e.g. impacts from wind, fire, flooding, excessive rainfall/snowfall etc.. - Provides partial but inadequate protections from climate change. | - Asset resiliency to environmental stresses is mostly or completely lacking; e.g. impacts from wind, fire, flooding, excessive rainfall/snowfall etc.. - Provides marginal or no protections from climate change
Notes: 1. | "Likelihood of Failure" is estimated as a percentage based on current status of asset performance.
2. | When assessing Performance of an entire Asset Class, rate where the balance of the assets score (either under one rating or between several).
3. | "Standards" can include measures set through internal poli+A5:F11cy, be an industry guideline, health and safety standard, a design, material or appearance standard, be a factor or measure as part of an Asset Levels of Service, or be an Asset Level of Service itself.

## 6. Water Performance Criteria
Asset Types | Notes on Performance Asset Levels of Service | ALOS | Criteria to Support ALOS Target1,2
- Transmission Mains - Feedermains - Local Watermains | A target of "Good" for the Performance Asset Levels of Service is recommended due to: - high importance to services - level of risk liability - the desire to provide efficient and effective service delivery at minimum cost - the necessity to meet regulatory requirements and/or design standards Where performance levels are assessed to be "Fair", it is likely that assets will continue to function adequately to meet minimum service requirements with possibly some limitations and elevated levels of risk and operating costs. Possible actions: Determine if a performance level of "Fair" is adequate for now and seek practical opportunities to rectify the deficiencies that are deemed feasible to address (e.g. when the asset is being replaced or reconstructed). Where performance levels are assessed to be "Poor" or "Very Poor" determine the most feasible and appropriate actions/improvements and implement at the earliest practical opportunity. | Operational Functionality | Efficient and effective service delivery: - Does not exceed recommended maximum pressures and flows - Minimal system leakage/water loss - Operates within recommended minimum and maximum pressures and flows during normal conditions - Stays within minimum and maximum velocities for various demand conditions - "Looped" water networks (to the extent possible) with flush points where dead-ends exist.
|  | Capacity to Meet Demands | Capacity to meet minimum service demands: - Able to provide adequate minimum pressures and flows for peak hour or maximum day plus fire demand conditions
|  | Operational Resiliency | - The distribution piping system should be designed to withstand the maximum operating pressures plus the transient pressures including negative pressures - Alternative supply points in the event of a feedermain break
- Pumping Stations/Booster Pumping and Pumping Systems - Standby Power - Surge protection systems/tanks | A target of "Good" for the Performance Asset Levels of Service is recommended due to: - high importance to services - level of risk liability - the desire to provide efficient and effective service delivery at minimum cost - the necessity to meet regulatory requirements and/or design standards Where performance levels are assessed to be "Fair", it is likely that assets will continue to function adequately to meet minimum service requirements with possibly some limitations and elevated levels of risk and operating costs. Possible actions: Determine if a performance level of "Fair" is adequate for now and seek practical opportunities to rectify the deficiencies that are deemed feasible to address (e.g. when the asset is being replaced or reconstructed). Where performance levels are assessed to be "Poor" or "Very Poor" determine the most feasible and appropriate actions/improvements and implement qt the earliest practical opportunity. | Operational Functionality | Efficient and effective service delivery and compliance with standards: - Does not exceed recommended maximum pressures and flows - Operates within recommended minimum and maximum pressures and flows during normal conditions - Suction and discharge stays within minimum and maximum velocities for various demand conditions - Systems and technology are efficient - Compliance with Provincial and Municipal Codes/Regulations (Ministry of Labour, Building, Fire and Electrical including Canadian Electrical Code (CSA C22.1-06)).
|  | Capacity to Meet Demands | Capacity to meet minimum service demands: - Able to provide adequate minimum pressures and flows for peak hour or maximum day plus fire demand conditions
|  | Operational Resiliency | - Pumping stations have "firm" pumping capacity - Adequate back-up capacity/units for critical pumping station processes - Adequate standby power generation capacity (e.g. Average day demand + power for process control + emergency lighting. (Requirements can be increased by municipalities) - Pumping systems and stations should be designed to minimize surges and transient pressure conditions including negative pressures - Adequate site and facility security
|  | Environmental Resiliency | - Pumping station facilities are protected from 100-year storm events - Climate change adaptation measures are in place
Surface Water Treatment Systems - Pre-Treatment/Pre-Treatment Systems - Primary Treatment/ Disinfection/ Primary Treatment Systems - Process treatment tanks/channels - Standby Power | A target of "Good" for the Performance Asset Levels of Service is recommended due to: - high importance to services - level of risk liability - the desire to provide efficient and effective service delivery at minimum cost - the necessity to meet regulatory requirements and/or design standards Where performance levels are assessed to be "Fair", it is likely that assets will continue to function adequately to meet minimum service requirements with possibly some limitations and elevated levels of risk and operating costs. Possible actions: Determine if a performance level of "Fair" is adequate for now and seek practical opportunities to rectify the deficiencies that are deemed feasible to address (e.g. when the asset is being replaced or reconstructed). Where performance levels are assessed to be "Poor" or "Very Poor" determine the most feasible and appropriate actions/improvements and implement at the earliest practical opportunity. | Operational Resiliency | Efficient and effective service delivery and compliance with standards: - Treatment design and operations maximize process efficiencies and effectiveness - Current systems and technology are efficient - Efficient and effective chemical application and disinfection processes - Does not exceed maximum treatment process velocities - Compliance with Provincial and Municipal Codes/Regulations (Ministry of Labour, Building, Fire and Electrical including Canadian Electrical Code (CSA C22.1-06)).
|  | Capacity to Meet Demands | Capacity to meet minimum service demands: - Able to provide adequate minimum treatment capacity for peak hour or maximum day plus fire demand conditions
|  | Operational Resiliency | Maintain full treatment capacity during emergency event/failure of treatment system components including: - Surplus hydraulic treatment capacity (up to 50%) - Back-up capacity/units for critical treatment processes - Adequate standby power generation capacity to maintain critical processes - Adequate site and facility security
|  | Environmental Resiliency | - Treatment facilities are protected from 100-year storm events - Climate change adaptation measures are in place
Groundwater Systems Wellhead pumping, treatment and Disinfection Systems including standby power | A target of "Good" for the Performance Asset Levels of Service is recommended due to: - high importance to services - level of risk liability - the desire to provide efficient and effective service delivery at minimum cost - the necessity to meet regulatory requirements and/or design standards Where performance levels are assessed to be "Fair", it is likely that assets will continue to function adequately to meet minimum service requirements with possibly some limitations and elevated levels of risk and operating costs. Possible actions: Determine if a performance level of "Fair" is adequate for now and seek practical opportunities to rectify the deficiencies that are deemed feasible to address (e.g. when the asset is being replaced or reconstructed). Where performance levels are assessed to be "Poor" or "Very Poor" determine the most feasible and appropriate actions/improvements and implement at the earliest practical opportunity. | Operational Resiliency | Efficient and effective service delivery and compliance with standards: - Treatment design and operations maximize process efficiencies and effectiveness - Current systems and technology are efficient - Efficient and effective chemical application and disinfection processes - Compliance with Provincial and Municipal Codes/Regulations (Ministry of Labour, Building, Fire and Electrical including Canadian Electrical Code (CSA C22.1-06)).
|  | Capacity to Meet Demands | Capacity to meet minimum service demands: - Able to provide adequate minimum treatment capacity for peak hour or maximum day plus fire demand conditions per small system design guidelines and where required.
|  | Operational Resiliency | Maintain full treatment capacity during emergency event/failure of treatment system component including: - Back-up capacity/units for critical treatment processes - Firm well pumping capacity - Adequate standby power generation capacity to maintain critical processes - Adequate site and facility security
|  | Environmental Resiliency | - Treatment facilities are protected from 100-year storm events - Adequate wellhead protection - Climate change adaptation measures are in place
Treated Water Storage | A target of "Good" for the Performance Asset Levels of Service is recommended due to: - high importance to services - level of risk liability - the desire to provide efficient and effective service delivery at minimum cost - the necessity to meet regulatory requirements and/or design standards Where performance levels are assessed to be "Fair", it is likely that assets will continue to function adequately to meet minimum service requirements with possibly some limitations and elevated levels of risk and operating costs. Possible actions: Determine if a performance level of "Fair" is adequate for now and seek practical opportunities to rectify the deficiencies that are deemed feasible to address (e.g. when the asset is being replaced or reconstructed). Where performance levels are assessed to be "Poor" or "Very Poor" determine the most feasible and appropriate actions/improvements and implement the earliest practical opportunity. | Operational Functionality | Efficient and effective service delivery and compliance with standards: - Water levels maintain minimum and maximum recommended normal operating pressures - Satisfies the recommendation that storage capacity should exceed the daily water supply capacity of the treatment plant plus fire flow demands (where fire flows are required) - Systems and technology are efficient - Efficient and effective chemical application and disinfection processes - Compliance with Ministry of Labour and Building Codes
|  | Capacity to Meet Demands | - Floating storage capacity requirements (Fire Storage + Equalization Storage (25% of maximum day demand) + Emergency Storage (25% of Fire Storage + Equalization Storage))
|  | Operational Resiliency | - Storage facilities are designed to maintain adequate pressure in the distribution system at average day demands in order to reduce the potential for groundwater intrusion and contamination of the system during a power failure or other emergency event. - Adequate site and facility security
|  | Environmental Resiliency | - Water storage facilities are protected from 100-year storm events - Climate change adaptation measures are in place
Notes: 1. | Consider the level of conformance to MOE Design Guidelines for Drinking-Water Systems for Operational Functionality, Capacity to meet Demands, Operational and Environmental Resiliency in the context of the "General Performance Ratings".
2. | This evaluation can be used: a) To inform a high-level "desktop exercise" to generally measure the ability of the asset classes to meet community service levels, or, b) To measure the performance of asset systems or assets to determine risk to services and the priority and scope of improvements. Independent professional assessments, flow measuring/monitoring and hydraulic modelling may be required, where practical and desirable to investigate asset class or individual asset compliance to ALOS criteria and levels of potential risk.

## 7. Water Asset Class Perf Eval
Asset Classes/Types7 | ALOS | Context for Evaluating Performance Criteria1 | Criteria to Support Proposed ALOS Target1, 2 (where information is available) | Weightings based on importance to ALOS4, 5 (Optional) | Distribution of Asset Ratings for each ALOS2, 3
[5 empty] | % Very Good | % Good | % Fair | % Poor | % Very Poor | % NA | TOTAL
- Transmission Mains - Feedermains | Operational Functionality | - Efficiency and effectiveness of service delivery - Ability to meet minimum current design and/or safety requirements - Level of operational problems experienced and whether they affect community services. - Compliance with current Regulations and/or Standards (including the level of "grandfathering") - Whether all required elements are present. | - Does not exceed recommended maximum pressures and flows
- Minimal system leakage/water loss
- Operates within recommended minimum and maximum pressures and flows during normal conditions
- Stays within minimum and maximum velocities for various demand conditions
- "Looped" water networks (to the extent possible) with flush points where dead-ends exist.
|  |  | Average Operational Functionality ALOS Ratings | 0 | [6 empty] | 0
|  |  | ALOS Rating - Operational Functionality |  | 0
| Capacity to Meet Demands | - To what degree capacity satisfies current demands and minimum community service levels - Level of operational problems experienced. - Are there noticeable negative affects on community service levels or stakeholders (residents and businesses) | - Able to provide adequate minimum pressures and flows for peak hour or maximum day plus fire demand conditions
- Other
|  |  | Average Capacity to Meet Demands ALOS Ratings | 0 | [6 empty] | 0
|  |  | ALOS Rating - Capacity to Meet Demands |  | 0
| Operational Resiliency | To what degree are minimum service requirements are maintained/protected with back-up systems, spare capacity or alternative supply. | - The distribution piping system should be designed to withstand the maximum operating pressures plus the transient pressures including negative pressures
- Alternative supply points in the event of a feedermain break
|  |  | Average Operational Resiliency ALOS Ratings | 0 | [6 empty] | 0
|  |  | ALOS Rating - Operational Resiliency |  | 0
Watermains | Operational Functionality | - Efficiency and effectiveness of service delivery - Ability to meet minimum current design and/or safety requirements - Level of operational problems experienced and whether they affect community services. - Compliance with current Regulations and/or Standards (including the level of "grandfathering") - Whether all required elements are present. | - Does not exceed recommended maximum pressures and flows
- Minimal system leakage/water loss
- Operates within recommended minimum and maximum pressures and flows during normal conditions
- Stays within minimum and maximum velocities for various demand conditions
- "Looped" water networks (to the extent possible) with flush points where dead-ends exist.
|  |  | Average Operational Functionality ALOS Ratings | 0 | [6 empty] | 0
|  |  | ALOS Rating - Operational Functionality |  | 0
| Capacity to Meet Demands | - To what degree capacity satisfies current demands and minimum community service levels - Level of operational problems experienced. - Are there noticeable negative affects on community service levels or stakeholders (residents and businesses) | - Able to provide adequate minimum pressures and flows for peak hour or maximum day plus fire demand conditions
- Other
|  |  | Average Capacity to Meet Demands ALOS Ratings | 0 | [6 empty] | 0
|  |  | ALOS Rating - Capacity to Meet Demands |  | 0
| Operational Resiliency | To what degree are minimum service requirements are maintained/protected with back-up systems, spare capacity or alternative supply. | - The distribution piping system should be designed to withstand the maximum operating pressures plus the transient pressures including negative pressures
- Other
|  |  | Average Operational Resiliency ALOS Ratings | 0 | [6 empty] | 0
|  |  | ALOS Rating - Operational Resiliency |  | 0
- Pumping Stations/Booster Pumping and Pumping Systems - Standby Power - Surge protection systems/tanks | Operational Functionality | - Efficiency and effectiveness of service delivery - Ability to meet minimum current design and/or safety requirements - Level of operational problems experienced and whether they affect community services. - Compliance with current Regulations and/or Standards (including the level of "grandfathering") - Whether all required elements are present. - Relevance and effectiveness of technology - Efficiency of resource consumption | - Does not exceed recommended maximum pressures and flows
- Operates within recommended minimum and maximum pressures and flows during normal conditions
- Suction and discharge stays within minimum and maximum velocities for various demand conditions
- Systems and technology are efficient
- Compliance with Provincial and Municipal Codes/Regulations (Ministry of Labour, Building, Fire and Electrical including Canadian Electrical Code (CSA C22.1-06)).
|  |  | Average Operational Functionality ALOS Ratings | 0 | [6 empty] | 0
|  |  | ALOS Rating - Operational Functionality |  | 0
| Capacity to Meet Demands | - To what degree capacity satisfies current demands and minimum community service levels - Level of operational problems experienced. - Are there noticeable negative affects on community service levels or stakeholders (residents and businesses) | - Able to provide adequate minimum pressures and flows for peak hour or maximum day plus fire demand conditions
- Other
|  |  | Average Capacity to Meet Demands ALOS Ratings | 0 | [6 empty] | 0
|  |  | ALOS Rating - Capacity to Meet Demands |  | 0
| Operational Resiliency | To what degree are minimum service requirements are maintained/protected with back-up systems, spare capacity or alternative supply. | - Pumping stations have "firm" pumping capacity
- Adequate back-up capacity/units for critical pumping station processes
- Adequate standby power generation capacity (e.g. Average day demand + power for process control + emergency lighting. (Requirements can be increased by municipalities)
- Pumping systems and stations should be designed to minimize surges and transient pressure conditions including negative pressures
|  | To what extent are the facilities secure from acts of vandalism, trespassing, theft, assault or terrorism. | - Adequate site security
|  |  | Average Operational Resiliency ALOS Ratings | 0 | [6 empty] | 0
|  |  | ALOS Rating - Operational Resiliency |  | 0
| Environmental Resiliency | To what extent the assets are resilient to environmental stresses; e.g. impacts from wind, fire, flooding, excessive rainfall/snowfall etc.. | - Pumping Station facilities are protected from 100-year storm events
|  | To what extent are the facilities resilient to climate change. | - Climate change adaptation measures are in place
|  |  | Average Environmental Resiliency ALOS Ratings | 0 | [6 empty] | 0
|  |  | ALOS Rating - Environmental Resiliency |  | 0
Surface Water Treatment Systems - Pre-Treatment/Pre-Treatment Systems - Primary Treatment/ Disinfection/ Primary Treatment Systems - Process treatment tanks/channels - Standby Power | Operational Functionality | - Efficiency and effectiveness of service delivery - Ability to meet minimum current design and/or safety requirements - Level of operational problems experienced and whether they affect community services. - Compliance with current Regulations and/or Standards (including the level of "grandfathering") - Whether all required elements are present. - Relevance and effectiveness of technology - Efficiency of resource consumption | - Treatment design and operations maximize process efficiencies and effectiveness
- Current systems and technology are efficient
- Efficient and effective chemical application and disinfection processes
- Does not exceed maximum treatment process velocities
- Compliance with Provincial and Municipal Codes/Regulations (Ministry of Labour, Building, Fire and Electrical including Canadian Electrical Code (CSA C22.1-06)).
|  |  | Average Operational Functionality ALOS Ratings | 0 | [6 empty] | 0
|  |  | ALOS Rating - Operational Functionality |  | 0
| Capacity to Meet Demands | - To what degree capacity satisfies current demands and minimum community service levels - Level of operational problems experienced. - Are there noticeable negative affects on community service levels or stakeholders (residents and businesses) | - Able to provide adequate minimum treatment capacity for peak hour or maximum day plus fire demand conditions
- Other
|  |  | Average Capacity to Meet Demands ALOS Ratings | 0 | [6 empty] | 0
|  |  | ALOS Rating - Capacity to Meet Demands |  | 0
| Operational Resiliency | To what degree are minimum service requirements are maintained/protected with back-up systems, spare capacity or alternative supply. | - Surplus hydraulic treatment capacity (up to 50%)
- Back-up capacity/units for critical treatment processes
- Adequate standby power generation capacity to maintain critical processes
|  | To what extent are the facilities secure from acts of vandalism, trespassing, theft, assault or terrorism. | - Adequate site security
|  |  | Average Operational Resiliency ALOS Ratings | 0 | [6 empty] | 0
|  |  | ALOS Rating - Operational Resiliency |  | 0
| Environmental Resiliency | To what extent the assets are resilient to environmental stresses; e.g. impacts from wind, fire, flooding, excessive rainfall/snowfall etc.. | - Treatment facilities are protected from 100-year storm events
|  | To what extent are the facilities resilient to climate change. | - Climate change adaptation measures are in place
|  |  | Average Environmental Resiliency ALOS Ratings | 0 | [6 empty] | 0
|  |  | ALOS Rating - Environmental Resiliency |  | 0
- Groundwater Systems - Wellhead pumping, treatment and disinfection systems including standby power | Operational Functionality | - Efficiency and effectiveness of service delivery - Ability to meet minimum current design and/or safety requirements - Level of operational problems experienced and whether they affect community services. - Compliance with current Regulations and/or Standards (including the level of "grandfathering") - Whether all required elements are present. - Relevance and effectiveness of technology - Efficiency of resource consumption | - Treatment design and operations maximize process efficiencies and effectiveness
- Current systems and technology are efficient
- Efficient and effective chemical application and disinfection processes
- Compliance with Provincial and Municipal Codes/Regulations (Ministry of Labour, Building, Fire and Electrical including Canadian Electrical Code (CSA C22.1-06)).
|  |  | Average Operational Functionality ALOS Ratings | 0 | [6 empty] | 0
|  |  | ALOS Rating - Operational Functionality |  | 0
| Capacity to Meet Demands | - To what degree capacity satisfies current demands and minimum community service levels - Level of operational problems experienced. - Are there noticeable negative affects on community service levels or stakeholders (residents and businesses) | - Able to provide adequate minimum treatment capacity for peak hour or maximum day plus fire demand conditions per small system design guidelines and where fire protection is required.
- Other
|  |  | Average Capacity to Meet Demands ALOS Ratings | 0 | [6 empty] | 0
|  |  | ALOS Rating - Capacity to Meet Demands |  | 0
| Operational Resiliency | To what degree are minimum service requirements are maintained/protected with back-up systems, spare capacity or alternative supply. | - Back-up capacity/units for critical treatment processes
- Firm well pumping capacity
- Adequate standby power generation capacity to maintain critical processes
|  | To what extent are the facilities secure from acts of vandalism, trespassing, theft, assault or terrorism. | - Adequate site security
|  |  | Average Operational Resiliency ALOS Ratings | 0 | [6 empty] | 0
|  |  | ALOS Rating - Operational Resiliency |  | 0
| Environmental Resiliency | To what extent the assets are resilient to environmental stresses; e.g. impacts from wind, fire, flooding, excessive rainfall/snowfall etc.. | - Well facilities are protected from 100-year storm events
- Adequate wellhead protection
|  | To what extent are the facilities resilient to climate change. | - Climate change adaptation measures are in place
|  |  | Average Environmental Resiliency ALOS Ratings | 0 | [6 empty] | 0
|  |  | ALOS Rating - Environmental Resiliency |  | 0
Treated Water Storage | Operational Functionality | - Efficiency and effectiveness of service delivery - Ability to meet minimum current design and/or safety requirements - Level of operational problems experienced and whether they affect community services. - Compliance with current Regulations and/or Standards (including the level of "grandfathering") - Whether all required elements are present. - Relevance and effectiveness of technology - Efficiency of resource consumption | - Water levels maintain minimum and maximum recommended normal operating pressures
- Satisfies the recommendation that storage capacity should exceed the daily water supply capacity of the treatment plant plus fire flow demands (where fire flows are required)
- Systems and technology are efficient
- Efficient and effective chemical application and disinfection processes
- Compliance with Ministry of Labour and Building Codes
|  |  | Average Operational Functionality ALOS Ratings | 0 | [6 empty] | 0
|  |  | ALOS Rating - Operational Functionality |  | 0
| Capacity to Meet Demands | - To what degree capacity satisfies current demands and minimum community service levels - Level of operational problems experienced. - Are there noticeable negative affects on community service levels or stakeholders (residents and businesses) | - Floating storage capacity requirements (Fire Storage + Equalization Storage (25% of maximum day demand) + Emergency Storage (25% of Fire Storage + Equalization Storage))
- Other
|  |  | Average Capacity to Meet Demands ALOS Ratings | 0 | [6 empty] | 0
|  |  | ALOS Rating - Capacity to Meet Demands |  | 0
| Operational Resiliency | To what degree are minimum service requirements are maintained/protected with back-up systems, spare capacity or alternative supply. | - Storage facilities are designed to maintain adequate pressure in the distribution system at average day demands in order to reduce the potential for groundwater intrusion and contamination of the system during a power failure or other emergency event.
|  | To what extent the assets are secure from acts of vandalism, trespassing, theft, assault or terrorism. | - Adequate site and facility security
|  |  | Average Operational Resiliency ALOS Ratings | 0 | [6 empty] | 0
|  |  | ALOS Rating - Operational Resiliency |  | 0
| Environmental Resiliency | To what extent the assets are resilient to environmental stresses; e.g. impacts from wind, fire, flooding, excessive rainfall/snowfall etc.. | - Water storage facilities are protected from 100-year storm events
|  | To what extent are the assets resilient to the affects of climate change. | - Climate change adaptation measures are in place
|  |  | Average Environmental Resiliency ALOS Ratings | 0 | [6 empty] | 0
|  |  | ALOS Rating - Environmental Resiliency |  | 0
Total Performance | [9 empty] | 0 | 0
0
Notes: 1. | Consider the level of conformance to MOE Design Guidelines for Drinking-Water Systems for Operational Functionality, Capacity to Meet Demands, Operational Resiliency and Environmental Resiliency in the context of the General Performance Ratings (Tab 5).
2. | This evaluation is intended as a "desktop exercise" to evaluate each asset class based on inherent knowledge of the system and its current ability to meet community service levels. Where information or experienced judgement is not available to assess some criteria or the criteria is not applicable, mark "100" under "NA" (Not Available/Applicable) to remove this criteria from the evaluation. Consider if the missing data or information should be included as part of a data collection plan.
3. | Distribute the different performance as a percentage of the entire Asset Class.
4. | ALOS Performance Weightings
Weightings
| 1 | Unimportant
| 2 | Relatively Unimportant
| 3 | Relatively Important
| 4 | Important
| 5 | Very Important
5. | If weightings are to be applied, they must be applied to ALL the asset performance ratings.
6. | If additional rows or columns are required to be added, the sheet needs to be "Unprotected". This will allow formulas to be copied and pasted. There is no password to Unprotect the sheet.
7. | This worksheet should be applied once for each Asset Class and replicated as often as necessary to evaluate each of the Asset Classes.

## 8. Water Asset Perf. Eval.
|  |  |  | Asset Name |  |  | Asset Name |  |  | Asset Name |  |  | Asset Name
Asset Types6 | ALOS | Context for Evaluating Performance Criteria1 | Criteria to Support Proposed ALOS Target1 (where information is available) | Weightings based on importance to ALOS2, 3 (Optional) | Asset Ratings for each ALOS4 | TOTAL | Weightings based on importance to ALOS2, 3 (Optional) | Asset Ratings for each ALOS4 | TOTAL | Weightings based on importance to ALOS2, 3 (Optional) | Asset Ratings for each ALOS4 | TOTAL | Weightings based on importance to ALOS2, 3 (Optional) | Asset Ratings for each ALOS4 | TOTAL
- Transmission Mains - Feedermains | Operational Functionality | - Efficiency and effectiveness of service delivery - Ability to meet minimum current design and/or safety requirements - Level of operational problems experienced and whether they affect community services. - Compliance with current Regulations and/or Standards (including the level of "grandfathering") - Whether all required elements are present. | - Does not exceed recommended maximum pressures and flows
- Minimal system leakage/water loss
- Operates within recommended minimum and maximum pressures and flows during normal conditions
- Stays within minimum and maximum velocities for various demand conditions
- "Looped" water networks (to the extent possible) with flush points where dead-ends exist.
|  |  | Average Operational Functionality ALOS Rating | 0 |  |  | 0 |  |  | 0 |  |  | 0
| Capacity to Meet Demands | - To what degree capacity satisfies current demands and minimum community service levels - Level of operational problems experienced. - Are there noticeable negative affects on community service levels or stakeholders (residents and businesses) | - Able to provide adequate minimum pressures and flows for peak hour or maximum day plus fire demand conditions
- Other
|  |  | Average Capacity to Meet Demands ALOS Rating | 0 |  |  | 0 |  |  | 0 |  |  | 0
| Operational Resiliency | To what degree are minimum service requirements are maintained/protected with back-up systems, spare capacity or alternative supply. | - The distribution piping system should be designed to withstand the maximum operating pressures plus the transient pressures including negative pressures
- Alternative supply points in the event of a feedermain break
|  |  | Average Operational Resiliency ALOS Rating | 0 |  |  | 0 |  |  | 0 |  |  | 0
- Local Watermains | Operational Functionality | - Efficiency and effectiveness of service delivery - Ability to meet minimum current design and/or safety requirements - Level of operational problems experienced and whether they affect community services. - Compliance with current Regulations and/or Standards (including the level of "grandfathering") - Whether all required elements are present. | - Does not exceed recommended maximum pressures and flows
- Minimal system leakage/water loss
- Operates within recommended minimum and maximum pressures and flows during normal conditions
- Stays within minimum and maximum velocities for various demand conditions
- "Looped" water networks (to the extent possible) with flush points where dead-ends exist.
|  |  | Average Operational Functionality ALOS Rating | 0 |  |  | 0 |  |  | 0 |  |  | 0
| Capacity to Meet Demands | - To what degree capacity satisfies current demands and minimum community service levels - Level of operational problems experienced. - Are there noticeable negative affects on community service levels or stakeholders (residents and businesses) | - Able to provide adequate minimum pressures and flows for peak hour or maximum day plus fire demand conditions
- Other
|  |  | Average Capacity to Meet Demands ALOS Rating | 0 |  |  | 0 |  |  | 0 |  |  | 0
| Operational Resiliency | To what degree are minimum service requirements are maintained/protected with back-up systems, spare capacity or alternative supply. | - The distribution piping system should be designed to withstand the maximum operating pressures plus the transient pressures including negative pressures
|  |  | Average Operational Resiliency ALOS Rating | 0 |  |  | 0 |  |  | 0 |  |  | 0
- Pumping Stations/Booster Pumping and Pumping Systems - Standby Power - Surge protection systems/tanks | Operational Functionality | - Efficiency and effectiveness of service delivery - Ability to meet minimum current design and/or safety requirements - Level of operational problems experienced and whether they affect community services. - Compliance with current Regulations and/or Standards (including the level of "grandfathering") - Whether all required elements are present. - Relevance and effectiveness of technology - Efficiency of resource consumption | - Does not exceed recommended maximum pressures and flows
- Operates within recommended minimum and maximum pressures and flows during normal conditions
- Suction and discharge stays within minimum and maximum velocities for various demand conditions
- Systems and technology are efficient
- Compliance with Provincial and Municipal Codes/Regulations (Ministry of Labour, Building, Fire and Electrical including Canadian Electrical Code (CSA C22.1-06)).
|  |  | Average Operational Functionality ALOS Rating | 0 |  |  | 0 |  |  | 0 |  |  | 0
| Capacity to Meet Demands | - To what degree capacity satisfies current demands and minimum community service levels - Level of operational problems experienced. - Are there noticeable negative affects on community service levels or stakeholders (residents and businesses) | - Able to provide adequate minimum pressures and flows for peak hour or maximum day plus fire demand conditions
- Other
|  |  | Average Capacity to Meet Demands ALOS Rating | 0 |  |  | 0 |  |  | 0 |  |  | 0
| Operational Resiliency | To what degree are minimum service requirements are maintained/protected with back-up systems, spare capacity or alternative supply. | - Pumping stations have "firm" pumping capacity
- Adequate back-up capacity/units for critical pumping station processes
- Adequate standby power generation capacity (e.g. Average day demand + power for process control + emergency lighting. (Requirements can be increased by municipalities)
- Pumping systems and stations should be designed to minimize surges and transient pressure conditions including negative pressures
|  | To what extent are the facilities secure from acts of vandalism, trespassing, theft, assault or terrorism. | - Adequate site and facility security
|  |  | Average Operational Resiliency ALOS Rating | 0 |  |  | 0 |  |  | 0 |  |  | 0
| Environmental Resiliency | To what extent the assets are resilient to environmental stresses; e.g. impacts from wind, fire, flooding, excessive rainfall/snowfall etc.. | - Pumping Station facilities are protected from 100-year storm events
|  | To what extent are the facilities resilient to climate change. | - Climate change adaptation measures are in place
|  |  | Average Environmental Resiliency ALOS Rating | 0 |  |  | 0 |  |  | 0 |  |  | 0
Surface Water Treatment Systems - Pre-Treatment/Pre-Treatment Systems - Primary Treatment/ Disinfection/ Primary Treatment Systems - Process treatment tanks/channels - Standby Power | Operational Functionality | - Efficiency and effectiveness of service delivery - Ability to meet minimum current design and/or safety requirements - Level of operational problems experienced and whether they affect community services. - Compliance with current Regulations and/or Standards (including the level of "grandfathering") - Whether all required elements are present. - Relevance and effectiveness of technology - Efficiency of resource consumption | - Treatment design and operations maximize process efficiencies and effectiveness
- Current systems and technology are efficient
- Efficient and effective chemical application and disinfection processes
- Does not exceed maximum treatment process velocities
- Compliance with Provincial and Municipal Codes/Regulations (Ministry of Labour, Building, Fire and Electrical including Canadian Electrical Code (CSA C22.1-06)).
|  |  | Average Operational Functionality ALOS Rating | 0 |  |  | 0 |  |  | 0 |  |  | 0
| Capacity to Meet Demands | - To what degree capacity satisfies current demands and minimum community service levels - Level of operational problems experienced. - Are there noticeable negative affects on community service levels or stakeholders (residents and businesses) | - Able to provide adequate minimum treatment capacity for peak hour or maximum day plus fire demand conditions
- Other
|  |  | Average Capacity to Meet Demands ALOS Rating | 0 |  |  | 0 |  |  | 0 |  |  | 0
| Operational Resiliency | To what degree are minimum service requirements are maintained/protected with back-up systems, spare capacity or alternative supply. | - Surplus hydraulic treatment capacity (up to 50%)
- Back-up capacity/units for critical treatment processes
- Adequate standby power generation capacity to maintain critical processes
|  | To what extent are the facilities secure from acts of vandalism, trespassing, theft, assault or terrorism. | - Adequate site and facility security
|  |  | Average Operational Resiliency ALOS Rating | 0 |  |  | 0 |  |  | 0 |  |  | 0
| Environmental Resiliency | To what extent the assets are resilient to environmental stresses; e.g. impacts from wind, fire, flooding, excessive rainfall/snowfall etc.. | - Treatment facilities are protected from 100-year storm events
|  | To what extent are the facilities resilient to climate change. | - Climate change adaptation measures are in place
|  |  | Average Environmental Resiliency ALOS Rating | 0 |  |  | 0 |  |  | 0 |  |  | 0
Groundwater Systems Wellhead pumping, treatment and Disinfection Systems including standby power | Operational Functionality | - Efficiency and effectiveness of service delivery - Ability to meet minimum current design and/or safety requirements - Level of operational problems experienced and whether they affect community services. - Compliance with current Regulations and/or Standards (including the level of "grandfathering") - Whether all required elements are present. - Relevance and effectiveness of technology - Efficiency of resource consumption | - Treatment design and operations maximize process efficiencies and effectiveness
- Current systems and technology are efficient
- Efficient and effective chemical application and disinfection processes
- Compliance with Provincial and Municipal Codes/Regulations (Ministry of Labour, Building, Fire and Electrical including Canadian Electrical Code (CSA C22.1-06)).
|  |  | Average Operational Functionality ALOS Rating | 0 |  |  | 0 |  |  | 0 |  |  | 0
| Capacity to Meet Demands | - To what degree capacity satisfies current demands and minimum community service levels - Level of operational problems experienced. - Are there noticeable negative affects on community service levels or stakeholders (residents and businesses) | - Able to provide adequate minimum treatment capacity for peak hour or maximum day plus fire demand conditions per small system design guidelines and where fire protection is required.
- Other
|  |  | Average Capacity to Meet Demands ALOS Rating | 0 |  |  | 0 |  |  | 0 |  |  | 0
| Operational Resiliency | To what degree are minimum service requirements are maintained/protected with back-up systems, spare capacity or alternative supply. | - Back-up capacity/units for critical treatment processes
- Firm well pumping capacity
- Adequate standby power generation capacity to maintain critical processes
|  | To what extent are the facilities secure from acts of vandalism, trespassing, theft, assault or terrorism. | - Adequate site security
|  |  | Average Operational Resiliency ALOS Rating | 0 |  |  | 0 |  |  | 0 |  |  | 0
| Environmental Resiliency | To what extent the assets are resilient to environmental stresses; e.g. impacts from wind, fire, flooding, excessive rainfall/snowfall etc.. | - Well facilities are protected from 100-year storm events
- Adequate wellhead protection
|  | To what extent are the facilities resilient to climate change. | - Climate change adaptation measures are in place
|  |  | Average Environmental Resiliency ALOS Rating | 0 |  |  | 0 |  |  | 0 |  |  | 0
Treated Water Storage | Operational Functionality | - Efficiency and effectiveness of service delivery - Ability to meet minimum current design and/or safety requirements - Level of operational problems experienced and whether they affect community services. - Compliance with current Regulations and/or Standards (including the level of "grandfathering") - Whether all required elements are present. - Relevance and effectiveness of technology - Efficiency of resource consumption | - Water levels maintain minimum and maximum recommended normal operating pressures
- Satisfies the recommendation that storage capacity should exceed the daily water supply capacity of the treatment plant plus fire flow demands (where fire flows are required)
- Systems and technology are efficient
- Efficient and effective chemical application and disinfection processes
- Compliance with Ministry of Labour and Building Codes
|  |  | Average Operational Functionality ALOS Rating | 0 |  |  | 0 |  |  | 0 |  |  | 0
| Capacity to Meet Demands | - To what degree capacity satisfies current demands and minimum community service levels - Level of operational problems experienced. - Are there noticeable negative affects on community service levels or stakeholders (residents and businesses) | - Floating storage capacity requirements (Fire Storage + Equalization Storage (25% of maximum day demand) + Emergency Storage (25% of Fire Storage + Equalization Storage))
- Other
|  |  | Average Capacity to Meet Demands ALOS Ratings | 0 |  |  | 0 |  |  | 0 |  |  | 0
| Operational Resiliency | To what degree are minimum service requirements are maintained/protected with back-up systems, spare capacity or alternative supply. | - Storage facilities are designed to maintain adequate pressure in the distribution system at average day demands in order to reduce the potential for groundwater intrusion and contamination of the system during a power failure or other emergency event.
|  | To what extent the assets are secure from acts of vandalism, trespassing, theft, assault or terrorism. | - Adequate site and facility security
|  |  | Average Operational Resiliency ALOS Ratings | 0 |  |  | 0 |  |  | 0 |  |  | 0
| Environmental Resiliency | To what extent the assets are resilient to environmental stresses; e.g. impacts from wind, fire, flooding, excessive rainfall/snowfall etc.. | - Water storage facilities are protected from 100-year storm events
|  | To what extent are the assets resilient to the affects of climate change. | - Climate change adaptation measures are in place
|  |  | Average Environmental Resiliency ALOS Rating | 0 |  |  | 0 |  |  | 0 |  |  | 0
Total Performance
Notes: 1. | Consider the level of conformance to MOE Design Guidelines for Drinking-Water Systems for Operational Functionality, Capacity to Meet Demands, Operational Resiliency and Environmental Resiliency in the context of the General Performance Ratings (Tab 5).
2. | ALOS Performance Weightings
Weightings
| 1 | Unimportant
| 2 | Relatively Unimportant
| 3 | Relatively Important
| 4 | Important
| 5 | Very Important
3. | If weightings are to be applied, they must be applied to ALL the asset performance ratings.
4. | ALOS Performance Ratings
| 1 | Very Good
| 2 | Good
| 3 | Fair
| 4 | Poor
| 5 | Very Poor
| 0 | N/A
5. | If additional rows or columns are required to be added, the sheet needs to be "Unprotected". When adding Rows, copy the row and paste between two criteria's by clicking "Insert Copied Row". This will allow formulas to be copied and pasted. There is no password to Unprotect the sheet.
6. | This worksheet can be used to evaluate up to four assets within the same Asset Class and the sheet can be replicated to evaluate additional assets.

## 9. General Asset Evaluation
Asset Name6 | ALOS | Performance Critera1 | Weightings based on importance to ALOS2, 3 (Optional) | Asset Ratings for each ALOS4 | TOTAL
| Operational Functionality | Efficiency and effectiveness of service delivery/provision
Ability to meet minimum current design and/or safety requirements
Level of operational problems experienced.
Level of noticeable affects to customers or services due to operational problems
Compliance with current Regulations and/or Standards (including levels of permitted "grandfathering")
Level/number of required elements present.
Relevance and effectiveness of technology
Efficiency of resource consumption
|  | Average Operational Functionality ALOS Rating | 0
| Capacity to Meet Demands | The degree to which capacity satisfies current demands and minimum community service levels
Level of operational problems related to capacity
Level of noticeable affects to customers due to capacity shortfall
|  | Average Capacity to Meet Demands ALOS Rating | 0
| Operational Resiliency | Level of surplus capacity for emergency or extraordinary operating conditions
Level of back-up capacity/units to maintain critical systems and services during emergency conditions.
Availability of alternative sources for emergency service provision
To what extent the assets are secure from acts of vandalism, trespassing, theft, assault or terrorism.
|  | Average Operational Resiliency ALSO Rating | 0
| Environmental Resiliency | To what extent the assets are resilient to environmental stresses; e.g. impacts from wind, fire, flooding, excessive rainfall/snowfall etc..
To what extent are the assets resilient to the affects of climate change.
|  | Average Environmental Resiliency ALOS Rating | 0
Total Performance |  |  |  | 0
Notes: 1. | Consider the level of conformance to Operational Functionality, Capacity to Meet Demands, Operational Resiliency and Environmental Resiliency in the context of the General Performance Ratings (Tab 5).
2. | ALOS Performance Weightings
Weightings
| 1 | Unimportant
| 2 | Relatively Unimportant
| 3 | Relatively Important
| 4 | Important
| 5 | Very Important
3. | If weightings are to be applied, they must be applied to ALL the asset performance ratings.
4. | ALOS Performance Ratings
| 1 | Very Good
| 2 | Good
| 3 | Fair
| 4 | Poor
| 5 | Very Poor
| 0 | N/A
5. | If additional rows or columns are required to be added, the sheet needs to be "Unprotected". When adding Rows, copy the row and paste between two criteria's by clicking "Insert Copied Row". This will allow formulas to be copied and pasted. There is no password to Unprotect the sheet.
6. | This worksheet should be applied once for each asset type and replicated as often as necessary or additional columns can be added for each additional asset in the Asset Class (formulas will be required to be copied over).

## A. Notes on Rating Watermains
ALOS Rating Method | Calculation Methodology | Advantages | Disadvantages
Rating = Pipe Age ALOS Target = Maximum Age | Pipes are normalized by age Pipe age and material (if available) is used a proxy to rate current and future pipe conditions. | - Most simple to use and rate. - Most municipalities have available data | - Least supportable measure for understanding current and future pipe conditions. - Age is an inaccurate proxy for actual pipe condition which can vary widely by age, pipe material, ground conditions and construction practices. - Not transferable to O.Reg 588/17 reporting requirements.
Rating = Number of lifetime breaks/km of pipe ALOS Target = Maximum lifetime pipe breaks/km of pipe | Pipe are normalized by lifetime breaks/km Current pipe condition rating = Number of lifetime breaks/km of main Estimated remaining useful service life = The average rate at which a watermain of a certain material breaks over its lifetime/km which is then used to estimate the number of years an average watermain lasts before reaching its target number of breaks. 1. Calculate the average rate at which a watermain of a certain material breaks over its lifetime. 2. Based on the current number of breaks for each watermain section, calculate the equivalent age of the watermain section and use that to estimate the remaining service life. If there are no breaks for a given watermain section, then estimate the remaining service life based on current age of the watermain and average time it takes to reach the target number of breaks. | - Better, more data driven predictor of pipe condition and estimated remaining useful service life than just pipe age alone - A more tangible measure of adequacy for service delivery | - Uses average historical break data which is still a proxy indicator of actual pipe conditions and remaining useful service life. - Requires more data and time to track pipe breaks and to correlate breaks with pipe age to extrapolate an estimated remaining useful service - It can take many years to assemble the data and history - Not transferable O.Reg 588/17 reporting requirements.
Rating = Hours of unplanned service interruptions/ section of pipe* ALOS Target = Maximum hours of unplanned service interruptions/section of pipe* *Hours of interruption = number of service connections affected by the pipe out of service (directly or indirectly connected) multiplied by the number of hours the pipe was out of service. | Pipes are normalized by number of affected services (directly or indirectly connected) per pipe section. Current pipe condition rating = Total number of hours a pipe section has been out of service multiplied by the number of services affected by the pipe interruption. Estimated remaining useful service life: 1. Calculate the average rate at which a watermain of a certain material breaks over its lifetime multiplied by the number of average hours to restore a broken watermain multiplied by the number of services affected by the watermain. 2. Based on the current number of breaks for each watermain section, calculate the equivalent age of the watermain section and estimate the remaining service life (the time at which the target for hours of interrupted service will be met). If there are no breaks for a given watermain section, then estimate the remaining service life based on current age of the watermain and average time it takes to reach the target hours of interrupted service base on number of breaks and number of affected service connections. Notes: 1. Affected connections can include services not directly connected to the pipe section i.e. connections affected "downstream" of a section break. 2. Pipe sections would be defined as node to node between controlling valve points 3. Km of pipe could be used in lieu of pipe sections but would not necessarily directly pinpoint more critical watermain sections. | - Better, more data driven predictor of pipe conditions, estimated remaining useful service life and service consequences than just pipe age - Can be used a measure of each pipe section's criticality: i.e. feedermains would potentially have many more hours of service interruption per pipe loss than a local watermain; thus, feedermains would naturally be more critical than local watermains and some sections of feedermains would be more critical than others. - The most tangible measure of service delivery - Easier to transfer to the O.Reg 588/17 reporting requirements. | - A more complicated data intensive measure of current and future pipe conditions than pipe age or number of pipe breaks ' - Requires a detailed inventory of the water system, locations of connections and valves and "downstream" modelling of services affected by pipe interruptions. ' - Uses average historical break and repair time data which is still a proxy indicator of actual pipe conditions and remaining useful service life. - It may take many years to assemble the data and history

## B. Water Summary ALOS Info
ALOS Type | Asset Categories | Rating Method | Distribution by Asset Ratings (Assets as a % of the Total Asset Class) and Corresponding Likelihood of Failure1
|  |  | Very Unlikely <10% | Unlikely 10%-30% | Possible 30%-60% | Likely 60%-90% | Very Likely >90%
Condition | All | Remaining Useful Service Life2 | >20 Years | 11-20 Years | 6-10 Years | 1-5 Years | <1 Year
| Civil Structures, Mechanical & Electrical Equipment | Generic Rating | Very Good | Good | Fair | Poor | Very Poor
|  | Description | - Fit for the future. - Well maintained, in good condition, new or recently rehabilitated. - Minor defects and/or wear | - Adequate for now. - Modest defects and/or wear. | - Shows signs of deterioration and some elements exhibit deficiencies. - May require attention. - Moderate defects and/or wear | - An increasing potential for asset conditions to affect the services it (or they) provides. - Approaching the end of service life. - The condition is below the standard and a large portion of the system (or asset) exhibits significant deterioration. - Significant defects and/or wear. | - Unfit for sustained service. - Near or beyond its expected service life and shows widespread signs of advanced deterioration. - The asset or some assets may be unusable. - Severe defects and/or wear
| Watermains | Breaks | <X Breaks | X to X Breaks | X to X Breaks | X to X Breaks | >X Breaks
Performance | All | Generic Rating | Very Good | Good | Fair | Poor | Very Poor
|  | General Description | Exceeds or fully meets performance requirements. No affect to services | Meets performance requirements. No affect to services | Just meets performance requirements with some limitations Minor or no perceivable affects to services. | Does not meet several performance requirements in whole or in part. Perceivable and/or sporadic affects to services | Does not meet many or most performance requirements as a whole. Moderate or significant and/or ongoing affects to services.
Notes: 1. | Likelihood of Failure is an estimate of the timespan (Condition) or the level of viability (Performance) that assets, asset components or asset systems are expected to provide adequate, safe and reliable Community Levels of Service (CLOS) but at increasing levels of risk as assets/asset components degrade as the end of service life approaches.
2. | The total lifespan of an asset often extends beyond Estimated Useful Service Life; however, the assets may no longer be sufficient, safe, viable, economical or reliable to provide safe and desired community services. Note that Likelihood of Failure provides high level estimates for strategic risk assessments purposes and can vary on an asset by asset basis according the environment, soil conditions, design, materials and use.

## C. ALOS Framework
AMONTario Asset Level of Service Framework
Condition Levels of Service (Tab 4) |  |  |  | Performance Levels of Service (Tabs 5-9)
ALOS Measures | Corresponding Likelihood of Failure Measures |  |  | ALOS Measures |  | Corresponding Likelihood of Failure Measures
PCI, BCI, FCI, PACP, General Ratings (“Very Good” to “Very Poor”), Maximum Age, etc. | Risk Ratings | Estimated Timeframe | % LoF | 1. Operational Functionality 2. Capacity to Meet Demands 3. Operational Resiliency 4. Environmental Resiliency | ALOS Rating | Risk Ratings | % LoF
| Very Unlikely | >20 yrs. | <10% |  | Very Good | Very Unlikely | <10%
| Unlikely | 11-20 yrs. | 10%-30% |  | Good | Unlikely | 10%-30%
| Possible | 6-10 yrs. | 30%-60% |  | Fair | Possible | 30%-60%
| Likely | 1-5 yrs. | 60%-90% |  | Poor | Likely | 60%-90%
| Very Likely or Certain | <1 yr. | >90% |  | Very Poor | Very Likely or Certain | >90%

## D. ALOS to CLOS Mapping
ALOS Categories | General ALOS Measurement Criteria | Predominant Community Service Outcomes
|  | Health & Safety | Reliability | Quality | Quantity | Efficiency | Accessibility
Condition | Physical state of the asset measured by condition rating systems (PCI, BCI, FCI, PACP, Number of Breaks, Very Good to Very Poor etc.) | X | X | X | X | X
Operational Functionality | - Efficiency and effectiveness of service delivery - Ability to meet minimum current design and/or safety requirements - Level of operational problems experienced and whether they affect community services. - Compliance with current Regulations and/or Standards (including the level of "grandfathering") - Whether all required elements are present. - Relevance and effectiveness of technology - Efficiency of resource consumption | X | X | X |  | X | X
Capacity to Meet Demands | - To what degree capacity satisfies current demands and minimum community service levels - Level of operational problems experienced. - Are there noticeable negative affects on community service levels or stakeholders (residents and businesses) | X | X | X | X | X | X
Operational Resiliency | - To what degree minimum service requirements are maintained/protected with back-up systems, spare capacity or alternative supply. - To what extent the assets are secure from acts of vandalism, trespassing, theft, assault or terrorism. | X | X
Environmental Resiliency | - To what extent the assets are resilient to environmental stresses; e.g. impacts from wind, fire, flooding, excessive rainfall/snowfall etc.. - To what extent are the assets resilient to the affects of climate change. | X | X |  |  |  | X